FORM Spec SLC-M, Revised 02/19	COPYRIGHT © 2018 SHIPPENSBURG PUMP COMPANY, INC. 
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED SPECIFICATIONS	SHIPCO® PUMPS
SUPPLEMENTAL NON-VACUUM BOILER FEED PUMPS SLC-FWS
CAPACITY SCHEDULE MUST BE COMPLETED.
Specification to be added to any boiler feed unit with a Control Panel that has an on off  
Furnish and install according to drawings and manufacturer’s instructions the quantity of (1) Shipco Logic Control System (SLC-FWS), electrical controls and accessories.
Nema 4x, 4" Color Touch Screen SLC will contain: Live Graphical and Numeric indication for constant water level and temperature. Operate solenoid valve based on water level. Provides an (optional) Emergency back-up solenoid control point based on water level.
Failure indication and protection as follows:
High high water alarm point indicates overflow condition
High water alarm point quickens response time
Low water alarm point quickens response time
Low low water alarm point indicates make-up failures
Low water cut-off point protects pumps from running dry 
High Temperature alarm point indicates trap or preheat assembly failure
Low Temperature alarm point indicates preheat assembly failure 
Alarm log automatically logs any irregular operating conditions
Loss of any sensor signal indicator
BacNet and Modbus Communications with shield wiring of 24 volt circuits. 
A Shipco® Nema 4x level and temperature transmitter needs to be used in lieu of float switches for alarm points, cut-off, plus both emergency and standard make-up to achieve the full potential of the SLC along with a temperature transmitter for data collection and maximum benefit.
A 24 Volt alarm button with silencing relay needs added to control panel.
Electrical control specifications must be added. See electrical specifications for boiler feed pumps. 
Manufacturer shall be Shipco® PUMPS, P.O. Box 279, Shippensburg, PA 17257.
Capacity Schedule (Required to complete suggested specifications).
Note: All Float switches are removed from specification.